To set up your Victron MultiPlus to use battery power during the day and recharge using off-peak grid power at night, you need to use the Energy Storage System (ESS) assistant and configure the Scheduled charge levels.

This configuration requires a Victron GX device (like a Cerbo GX or Color Control GX) and an MK3-USB adapter for initial setup with a computer.

Step 1: Install and Configure ESS Assistant

- Update Firmware: Ensure all your Victron equipment (MultiPlus, GX device, etc.) has the latest firmware installed.

- Connect Hardware: Use an MK3-USB adapter to connect your MultiPlus to a computer running the VEConfigure software or use the VictronConnect app if compatible with your MultiPlus model via the dongle.

- Load ESS Assistant: In VEConfigure, go to the "Assistants" tab and load the ESS (Energy Storage System) Assistant. This is the core functionality for managing energy flow between the grid, battery, and loads.

- Set ESS Mode: Within the ESS settings in your GX device menu, select one of the "Optimized" modes (with or without BatteryLife, depending on your battery type and preference). This mode prioritizes self-consumption, using PV power first, then battery power, and only importing from the grid when necessary.

- Set Minimum SoC: Configure the Minimum SoC (unless grid fails) to a desired level (e.g., 10-20%). The system will stop discharging the battery from the grid when this limit is reached, switching to grid power for loads. In a grid failure, it will continue discharging past this point until other low voltage thresholds are met.

Step 2: Configure Scheduled Charging (Time-of-Use)

This is done directly on the GX device interface (e.g., Cerbo GX display or remote console via VRM portal).

- Navigate to ESS Menu: On your GX device, go to Settings → ESS.

- Access Scheduled Charge Levels: Find the Scheduled charge levels option in the ESS menu.

- Set Off-Peak Schedule:

  - Create a new schedule entry corresponding to your off-peak electricity tariff times (e.g., midnight to 6 AM).

  - Set the SoC limit (target) for this period to 100% (or your battery manufacturer's recommended full charge target).

  - This tells the system to use grid power to charge the battery to 100% during this specific time window, ensuring it is full for daily use.

- Set Peak/Daytime Behavior:

  - During non-scheduled "peak" or daytime hours, the ESS will default back to its "Optimized (self-consumption)" mode.

  - It will prioritize using stored battery power (down to your set Minimum SoC) and available solar power to run your loads before importing expensive peak-rate grid power.

  - You can set the "Self-consumption above limit" to "PV & Battery" during the day to allow discharge from the battery for self-consumption.

Summary of Operation

- During Off-Peak Hours: The system charges the battery from the grid to 100% SoC.

- During Peak Hours/Daytime: The system runs loads from solar and the battery (self-consumption) until the minimum SoC is reached, then uses grid power if needed.

This setup effectively minimizes the amount of high-cost peak-rate electricity you use and maximizes the use of stored, low-cost (or free solar) energy.